## Slide 1: Operating “New” Multiple Hearth Incinerators
40 CFR Subpart LLLL

## Slide 2: “New” MHI emissions limits
Chart: MMMM vs. LLLL
| PM | CO | NOx | SO2 | Hg | Pb | Cd | HCl | D/F (TEQ) | D/F (TMB)
 | 0.25 | 0.98632 | 0.045455 | 0 | 0.46429 | 0.98833 | 0.97474 | 0 | 0.99313 | 0.991
52 PPM CO
210 PPM NOX
2.4 µg/DSCM Cadmium
3.5 µg/DSCM Lead
45 pg/DSCM D/F (TMB)
2.2 pg/DSCM D/F (TEQ)
% Emissions Reduction (existing to “new”)
Notes: 1. CEG acquired wastewater in 2012, NSPS and EG were finalized in 2011. Rulemaking required by court order to address Urban Air Toxics from §112 area sources.
2. The MHI were due for a rebuild. Considered doing everything but continuing to incinerate. Sought design to meet limits: CO controlled with RTO. Cadmium/Lead controlled with WESP. D/F controlled with RTO and Carbon Adsorber. None of these controls were considered in the NSPS.

## Slide 3: System Overview
Rehab/
Replace
New

## Slide 4: Operating Limits
  Part 60 requires demonstration of continuous compliance with operating limits or CEMS, including startup, shutdown and malfunction
  Stack Testing sets operating limits that each MHI must stay within following stack testing
  Use of bypass stack prohibited
Operating Parameter | Compliance Period
Carbon Monoxide CEMS | 24 hour block average
Hearth 1 Temperature | 12 hour block average
Scrubber Pressure Drop | 12 hour block average
Scrubber Water Flow Rate | 12 hour block average
Scrubber Water Drain pH | 3 hour block average
WESP Power | 12 hour block average
WESP Flush Water Flow | 12 hour block average
RTO Temperature | 3 hour block average
RTO Flue Gas Flow | Once per day
Carbon Adsorber Pressure Drop | Once per day
Notes: Difficulties: Establishing wide enough ranges to make it possible for continuous compliance while demonstrating compliance with the emissions limits. Protection of the control equipment and life safety necessitates use of the bypass damper. Continuous compliance during startup and shutdown is difficult: air flow, excess oxygen, low temperatures. All these deviations require a significant amount of reporting followed by extensive settlement discussions with the state. 5-year renewal has taken >200 hours of review prior to public notice and comment to limit unnecessary state conditions for continuous compliance, monitoring and compliance demonstrations.

## Slide 5: More Equipment, More Maintenance!
Carbon Adsorber maintenance
Carbon replacement frequency
Driven by parametric monitoring parameter
Driven by failed stack test
Driven by carbon material analysis
RTO maintenance
RTO cleaning (driven by parametric monitoring parameter)
Silicon dioxide
Refractory challenges and replacement frequency
Outdoor equipment and the elements
Freezing
Condensation

## Slide 6: Maintenance Plan Development
New emissions permit drove development of maintenance plan
Basic plan developed from OEM guidelines
Settled on semi-annual cadence of major maintenance outages to preform maintenance tasks
Key activities
  Permit required semiannual instrument calibrations on RTD’s, Diff Pressures and flows
  Cleaning and inspection of WESP, RTO, Packed Tower, Incinerator refractory and bypass dampener
  Safety and performance inspections of burners
  Sensing lines
  Heat trace and insulation

## Slide 7: Maintenance Costs Increases
Chart: Total Annual Incineration Maintenance Costs per Year 2012 to 2018
| 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018
Total | 677445.45 | 604546.16 | 619039.38 | 556971.24 | 744847.23 | 1047961.95 | 928386.19

## Slide 8: Operational Challenges
Juggling Parametric Monitoring limits
  Scrubber Water Drain pH
    Source water pH fluctuates seasonally
    Feed rate and sludge characteristics vary continuously
  System Flow and Differential Pressures
    Sludge moisture content and feed rate affect air flow
    Seasonal ambient air temperatures
Notes: Scrubber water pH control was a known challenge going into this project. Two systems were installed for pH control but both systems were largely unsuccessful. pH control is handled by reducing the feed to reduce the acid gas capture.
Airflow through the system must stay in the range set forth during stack testing. However, differential pressures throughout the system also need to be maintained within the parametric monitoring limits and the equipment safety limits. This can make things very difficult on the operators.

## Slide 9: Control System & Operational Improvements
Limiting Emergency Bypass Events
  Increasing dependability without compromising safety
Limiting Parametric Monitoring Deviations
  Block averages can be tricky w/r/t taking units in and out of service
  Putting meaningful data in front of Operators
  Ensuring that compliance stack tests are representative of the full gamut of operational conditions
    Running the Induced Draft fan at low/normal/high speed throughout stack testing creates parametric monitoring ranges that are less restrictive

## Slide 10: Operational & System Improvements
  New tools had to be created to help Operators track block averages throughout overlapping shifts
  PLC programming had to be modified so that bypassing the emissions control equipment was the last resort