## Slide 1
City of Columbus
Department of Public Utilities
Division of Sewerage & Drainage
Southwesterly Composting Facility
Odor Reduction Improvements Project
September 4, 2019

## Slide 2
Agenda
  Columbus Biosolids Management Program
  Southwesterly Composting / ‘Compost Facility’
  Odor Reduction Improvements Project
  Project Lessons Learned

## Slide 3
Columbus Biosolids Management Program

## Slide 4
DOSD Overview
Jackson Pike WWTP
  150 mgd peak
  45% of Treated Flow
Southerly WWTP
  330 mgd peak + 110 CEPT (4Q19)
  55% of Treated Flow
Compost Facility
  200 wtpd
  33% - 50% total solids produced
COMPOST
``
SOUTHERLY
``
JACKSON PIKE

## Slide 5
Residuals Mgr
Josh Lutz
Soil Application Coordination
Heather Curtis
Compost
2 Supervisors
12 Equip Operators
4 Support
Commercial Digestion
Contractor
Land Application
Contractor
Tree Farm
Contractor
Emergency and Smaller Outlets
Biosolids Management Overview
Traditional Activated Sludge WWTPs
  Class B Anaerobic Digestion to Thickening or Dewatering
  Intermittent Unclassified WAS to Dewatering
Residuals Management
  24,000 dry tons of biosolids per year
  4 Primary Outlets
  Incineration Ceased in 2015
  Landfilling Ceased in 2016

## Slide 6
Biosolids Management Outlets
Land Application: Class B Liquid
Deep Row Tree Farms: Class B Cake
Commercial Digesters Feedstock (& Land App): CLB/UNCL Cake
Class A Compost, Com-Til: CLB/UNCL Cake
2018, DT
2019 Jan-May, DT

## Slide 7
Solids Management Program Overview - Current
UNCLASSIFIED
SOLIDS
CLASS B
BIOSOLIDS
THICKENING
DEWATERING
DEWATERING
TREE
FARMS
COMMERCIAL
DIGESTION
COMPOST
FACILITY
(JP Only)
AG LAND
APPLICATION
EMERGENCY
TO LANDFILL

## Slide 8
Biosolids Program Drivers
Continue a 100% Beneficial Use Program
Lower long-term costs / steady sewer rates
Recycling organics back to environment
Transition mindsets to think of biosolids as a commodity
Outlet diversity to increase reliability

## Slide 9
Biosolids Program Changes & Challenges
Less Land & Fewer Days: weather, change in agricultural practices, less winter wheat recently
Keeping Vendors Fed: Such as thing as “too many” outlets?
Wet Weather: Plant Production, Outlet Reliability
Managing Outlet Performance
  Vendor contracts
  Truck management
  Matching outlets to plant production
New Ohio regulations for on-site storage, application, monitoring and recordkeeping

## Slide 10
Compost Facility
Background

## Slide 11
Compost
Facility
Notes: -Compost Facility to the west of Southerly
-45 acres fences surrounded by approximately 400 acres of City owned farmland

## Slide 12
Compost Facility – Background
Site developed in 1980 using static pile composting
Several projects completed in 1980’s increased efficiency and capacity
Due to odor complaints from static pile composting, the site switched to negative aerated static pile composting in 2001
  160 wtpd average, 200 wtpd peak capacity, 7 – 9 trucks /day
  Two pads with dedicated biofilters
  44 legs per pad, 3 trucks per leg
Notes: -Compost Facility to the west of Southerly
-45 acres fences surrounded by approximately 400 acres of City owned farmland

## Slide 13
Composting Pad 2 and Biofilter 2
Notes: -Compost Facility to the west of Southerly
-45 acres fences surrounded by approximately 400 acres of City owned farmland

## Slide 14
Composting Pad and Biofilter
Notes: -Compost Facility to the west of Southerly
-45 acres fences surrounded by approximately 400 acres of City owned farmland

## Slide 15
Compost Facility - Operations
Compost Process Steps:
  Mixing
  Composting
  Curing
  Screening & Woodchip Recycling
  Finished Product
Support Functions:
  Leachate Management
  Air Pollution & Odor Control
  Bulking Agent
Notes: -Compost Facility to the west of Southerly
-45 acres fences surrounded by approximately 400 acres of City owned farmland

## Slide 16: Compost Facility – Process Diagram

## Slide 17
Compost Facility - Benefits
Class A, Exceptional Quality Product
Triple Threat! - Processing, Storage, &
Beneficial Use Outlet
Revenue Stream: They pay Us to take it!
  $12 - $19/CY
Simple operations and equipment
Wide spot in biosolids program able to
ramp up & down
Reliable during wet weather
Accepts Class B and Unclassified
City-Controlled!
Notes: -Compost Facility to the west of Southerly
-45 acres fences surrounded by approximately 400 acres of City owned farmland

## Slide 18
Odor Reduction Improvements

## Slide 19
Update technology and techniques to reduce odors
Be the best neighbor possible
Aeration equipment at end of useful life
Restore flexibility lost with Incinerators
Increase resiliency for wet weather and outlet underperformance
Continue average growth, allow for 150% increase to peak
Odor Reduction Improvements
Project Drivers

## Slide 20
Compost Facility – Existing Site
COMPOST PAD 1
COMPOST PAD 2
BIOFILTERS
CURING
CURING
COMTIL
SCREEN
SCREEN
STAGING
HEADERS

## Slide 21
Add 3rd Pad & Biofilter
Increase capacity from
200 to 300 wtpd
$8M CCE
Planning started 1Q2017
Odor Reduction Improvements
Project Description
Day 1

## Slide 22
Compost Facility – Project Plan Day 1
COMPOST PAD 1
COMPOST PAD 2
BIOFILTERS
CURING
COMTIL
STAGING
COMPOST PAD 0

## Slide 23
Compost Facility – Project Challenges
Increased capacity, reduced footprint
Tight logistics; semis, screens and 160’ headers
Limited compost staging area
Haul distance & number of trips
Aged, “patch-worked” electrical
infrastructure
Stormwater Regulations
Notes: -Compost Facility to the west of Southerly
-45 acres fences surrounded by approximately 400 acres of City owned farmland

## Slide 24
Compost Facility – Updated Project Plan
MATERIAL STOCKPILES
LEACHATE LAGOON EXPANSION
BIOFILTERS
PAD 3
PAD 2
PAD 1
STAGING
COVERED MATERIAL STORAGE
CURING

## Slide 25
Demolished 2 pads & Construct 3 in new location
Maintained process type and pile geometry
Updated technology and techniques
Common bank of biofilters (vs. dedicated)
Open space on compost pad used for aerated curing
$38M CCE
Phase II planned for work that got cut
Accommodate future ammonia scrubber and 4th pad
Odor Reduction Improvements
Project Description – Day 1,125

## Slide 26
Composting Process
Curing
Monitoring & Control
Leachate Management
Biofilter
Odor Reduction Improvements

## Slide 27
Composting Process Improvements
  Pile geometry, configuration and pile recipe largely unchanged
  Increased air rate and defined the demand curve
  Engineered header
  Improved leachate management in pile
Odor Reduction Improvements

## Slide 28
A Third Pad = Better Curing
Increased peak capacity
Provides aerated curing during average periods
  More consistent product
  Increased VS reduction
  Greater moisture removal
  Better compost maturity
  Evens out load to biofilter
Odor Reduction Improvements

## Slide 29
Monitoring & Control
Automated control during non-staffed hours via motorized valves
Match air rates to demand
Balance biofilter needs with foul air supply
Odor Reduction Improvements

## Slide 30
Leachate Management
In pipe, free drainage & precipitation runoff
Odor Reduction Improvements

## Slide 31
Remove moisture in pipe before pile blowers
Add drain point in settling zone for free drainage.
Plumbed drains and increased air flow will reduce free drainage
Improved leachate removal reduces anaerobic conditions
Odor Reduction Improvements
Leachate Management Improvements include:

## Slide 32
Update leachate lagoon to current code
  Discharge to sanitary sewer
  6’ Deep
  Restrict effluent to match sewer capacity
  Negligable leachate during dry weather
  During wet weather, leachate regulated as contaminated stormwater
Odor Reduction Improvements
Existing | Proposed
1.5 MG | 5 MG
2.5 Year Storm Event | 100 Year Storm Event
0.5 Overflows / year | No Overflows
Pump Station Conveyance | Gravity Sewer Outfall

## Slide 33
Biofilter
  Optimized size
  Common interconnected header to balance loading
  Maintenance friendly, facilitates timely rehab
  Process improvements anticipated to benefit biofilters; lower ammonia will result in better bacteria for odor control
Odor Reduction Improvements

## Slide 34
Lessons Learned

## Slide 35
Big Picture; balancing Capital with Operating
Unusual
Planning Stage
  Scientific basis vs. precedent
  Finalize concepts
  Process approach vs. cost iterations
Design
  Permit coordination
Construction
  See you in Cincinnati 2020!
Odor Reduction Improvements –
Lessons Learned

## Slide 36
Thank you!
Questions?
PLEiden@columbus.gov
Tours Welcome!
7000 Jackson Pike, Lockbourne, Ohio 43137
Lutz@columbus.gov
September 4, 2019